## MV BoQ
SACELLE WIND FARM. ELECTRIC WORKS BOQ
00. Design
ITEM | UNIT | DESCRIPTION
00.01 | un | Execution Design and As built for MV network
01. CABLE TRENCH
ITEM | UNIT | DESCRIPTION
01.01 | m³ | Site clearing and topsoil stripping by mechanical methods, including topsoil excavation, bush and tree cutting, stump extraction, loading and transport to dump or acredited site. Include topsoil stockpiling near access roads for subsequent slope revegetation. Average depth 20 cm, width 3 m.
01.02 | m | Execution and supply of the necessary materials for the construction of a cable trench to house 1 medium voltage circuit, 1 fiber optic cable and grounding conductor on the side of roads or cross country. Including excavation in compacted soil and/or rock, with mechanical means (backhoe, hammer, etc.) for cable trenches, including loading and transport on truck of products to place of use or landfill. Includes compaction of the base, supply and placement of river washed sand backfill over the MV cables and backfill compacted with the selected soil from the excavation. Includes supply and placement of standardized plastic signaling tape, buried in electrical cable trenches, and prefabricated halogen-free plastic plate as mechanical protection. In accordance with project drawings. Trench type A (0.40 m wide x 1.20 m depth)
01.03 | m | Execution and supply of the necessary materials for the construction of a cable trench to house 2 medium voltage circuits, 2 fiber optic cables and grounding conductor on the side of roads or cross country. Including excavation in compacted soil and/or rock, with mechanical means (backhoe, hammer, etc.) for cable trenches, including loading and transport on truck of products to place of use or landfill. Includes compaction of the base, supply and placement of river washed sand backfill over the MV cables and backfill compacted with the selected soil from the excavation. Includes supply and placement of standardized plastic signaling tape, buried in electrical cable trenches, and prefabricated halogen-free plastic plate as mechanical protection. In accordance with project drawings. Trench type B (0.60 m wide x 1.20 m depth)
01.04 | m | Execution and supply of the necessary materials for the construction of a cable trench to house 3 medium voltage circuits, 3 fiber optic cables and grounding conductor on the side of roads or cross country. Including excavation in compacted soil and/or rock, with mechanical means (backhoe, hammer, etc.) for cable trenches, including loading and transport on truck of products to place of use or landfill. Includes compaction of the base, supply and placement of river washed sand backfill over the MV cables and backfill compacted with the selected soil from the excavation. Includes supply and placement of standardized plastic signaling tape, buried in electrical cable trenches, and prefabricated halogen-free plastic plate as mechanical protection. In accordance with project drawings. Trench type C (1.00 m wide x 1.20 m depth)
01.05 | m | Execution and supply of materials necessary for the construction of a cable trench to house 1 medium voltage circuit, 1 fiber optic cable and grounding conductor at road and drainage crossings. Including excavation in compacted soil and/or rock, with mechanical means (backhoe, hammer, etc.) for cable trenches, including loading and transport by truck of the excavation products to the place of use or landfill. Includes compaction of the base, supply and placement of Ø200 and Ø90 pipes, mass concrete fc'=200 kg/cm², compacted backfill with the selected soil from the excavation, supply and placement of standardized plastic signaling tape, supply and backfill of road surfacing material. In accordance with the project drawings. Trench type D (0.70 m wide x 1.20 m depth)
01.06 | m | Execution and supply of materials necessary for the construction of a cable trench to house 2 medium voltage circuits, 2 fiber optic cables and grounding conductor at road and drainage crossings. Including excavation in compacted soil and/or rock, with mechanical means (backhoe, hammer, etc.) for cable trenches, including loading and transport by truck of the excavation products to the place of use or landfill. Includes compaction of the base, supply and placement of Ø200 and Ø90 pipes, mass concrete fc'=200 kg/cm², compacted backfill with the selected soil from the excavation, supply and placement of standardized plastic signaling tape, supply and backfill of road surfacing material. In accordance with the project drawings. Trench type E (1.10 m wide x 1.20 m depth)
01.07 | m | Execution and supply of materials necessary for the construction of a cable trench to house 3 medium voltage circuits, 3 fiber optic cables and grounding conductor at road and drainage crossings. Including excavation in compacted soil and/or rock, with mechanical means (backhoe, hammer, etc.) for cable trenches, including loading and transport by truck of the excavation products to the place of use or landfill. Includes compaction of the base, supply and placement of Ø200 and Ø40 pipes, mass concrete fc'=200 kg/cm², compacted backfill with the selected soil from the excavation, supply and placement of standardized plastic signaling tape, supply and backfill of road surfacing material. In accordance with the project drawings. Trench type F (0.70 m wide x 1.40 m depth)
01.08 | m | Execution and supply of necessary materials for the construction of a cable trench to house cables in a gas pipeline crossing. Including excavation in compacted soil and/or rock, with mechanical means (backhoe, hammer, etc.) for cable trenches, including loading and transportation by truck of the excavation products to the place of use or landfill. Includes compaction of the base, supply and placement of Ø200 and Ø90 pipes, mass concrete fc'=150 kg/cm², backfill compacted with the selected soil from the excavation. In accordance with the project drawings.
01.09 | m | Execution and supply for the execution of a cable passage under water stream, executed by driving, including 600 mm steel pipe with the upper outer generatrix of the pipe at a minimum depth of 2 m under the bottom of the riverbed. Including Ø200 and Ø90 subducts, including the complete execution of the attack and exit wells, and manholes. It includes the installation of a protection sheath until exceeding the road easement zone on both margins (pipe of the same characteristics as that of the jacking, welded on each side of the jacking). In accordance with the project drawings.
01.10 | un | Cable route and change of direction marker, prefabricated, placed on a concrete bed every 200 m, including excavation, cleaning and finishing, completely finished.
01.11 | un | Ball marker locator, long range RFID reader/writer for the location and programming of passive buried tags.
02. CABLING
ITEM | UNIT | DESCRIPTION
02.01 | m | Supply and laying of single-pole aluminum XLPE 70 mm², with metallic shield. According to standards, specifications, and drawings.
02.02 | m | Supply and laying of single-pole aluminum XLPE 185 mm², with metallic shield. According to standards, specifications, and drawings.
02.03 | m | Supply and laying of single-pole aluminum XLPE 240 mm², with metallic shield. According to standards, specifications, and drawings.
02.04 | m | Supply and laying of single-pole aluminum XLPE 630 mm², with metallic shield. According to standards, specifications, and drawings.
02.05 | un | Supply and execution of single-pole joints for 70 mm² cable, the number of these being the minimum necessary and always subject to the approval of the property. Completely installed and connected. Note. joints are for 1000m cable reel consideration.
02.06 | un | Supply and execution of single-pole joints for 185 mm² cable, the number of these being the minimum necessary and always subject to the approval of the property. Completely installed and connected. Note. joints are for 1000m cable reel consideration.
02.07 | un | Supply and execution of single-pole joints for 240 mm² cable, the number of these being the minimum necessary and always subject to the approval of the property. Completely installed and connected. Note. joints are for 1000m cable reel consideration.
02.08 | un | Supply and execution of single-pole joints for 630 mm² cable, the number of these being the minimum necessary and always subject to the approval of the property. Completely installed and connected. Note. joints are for 1000m cable reel consideration.
02.09 | un | Single-pole connector (material+assembly) connecting wind turbine switchgear or substation switchgear for aluminum 70 mm² cable, according to standards and specifications, and according to drawings.
02.10 | un | Single-pole connector (material+assembly) connecting wind turbine switchgear or substation switchgear for aluminum 185 mm² cable, according to standards and specifications, and according to drawings.
02.11 | un | Single-pole connector (material+assembly) connecting wind turbine switchgear or substation switchgear for aluminum 240 mm² cable, according to standards and specifications, and according to drawings.
02.12 | un | Single-pole connector (material+assembly) connecting wind turbine switchgear or substation switchgear for aluminum 630 mm² cable, according to standards and specifications, and according to drawings.
03. EARTHING GRID
ITEM | UNIT | DESCRIPTION
03.01 | m | Supply and laying of earthing cable based on bare copper 50 mm² conductor, p/p of aluminothermic welding from each wind turbine, sectionable boxes for grounding measurement, small material and connections, according to manufacturer's specifications, standards and drawings.
03.02 | ud | Wind turbine grounding for conventional foundation. Supply and laying of 50 mm² bare copper conductor (85 m for perimeter ring, 21,6 m for outer ring and 35 m for radial conductors); 9 Cadwell aluminothermic welding; 4 copper to copper mechanical connectors, 3 steel bars and soldering to the foundation rebar, 3 copper to steel bar mechanical connectors; main earthing plate; small material and connection to the main wind farm earthing, carried out according to technologist specifications, standards, drawings and as described in the manufacturer specification. It includes the protection of the bare copper cable in the bottom of the excavation with suitable backfill and tubes for the passage of grounding cables without contact with the concrete.
03.03 | ud | Wind turbine grounding for pile foundation. Supply and laying of 50 mm² bare copper conductor (80,4 m for perimeter ring, 21,4 m for outer ring and 33 m for radial conductors); 9 Cadwell aluminothermic welding; 4 copper to copper mechanical connectors, 3 steel bars and soldering to the foundation rebar, 3 copper to steel bar mechanical connectors; main earthing plate; small material and connection to the wind farm main earthing, carried out according to technologist specifications, standards, drawings and as described in the manufacturer specification. It includes the protection of the bare copper cable in the bottom of the excavation with suitable backfill and tubes for the passage of grounding cables without contact with the concrete.
04. FIBER OPTIC NETWORK
ITEM | UNIT | DESCRIPTION
04.01 | m | Supply and laying of signal and data transmission line for control, maneuver and automation, based on 9/125 µm singlemode fiber cable, fiberglass armor, with 12 fibers, loose structure provided with protection against humidity and rodents, according to applicable standards and specifications and according to drawings.
04.02 | ud | Connectorization of optical fibers for wind turbines and substation. Including connectors for 24 fibers for each cable entry to the the wind turbine, connectorization box with capacity for 24 units, interconnection pig-tails between the previous box and the connectors of the low voltage control cabinet communications equipment. It includes the supply of 24 pig-tails (female-female) for each optical fiber loop jumper in case of absence of aero power supply. Including those necessary for the connection to the substation communications equipment and the execution of the necessary fiber optic joints.
TOTAL

## CIVIL BoQ
SACELLE WIND FARM (ROMANIA) CIVIL WORKS BOQ
00. Design
ITEM | UNIT | DESCRIPTION
00.01 | un | Execution Design and As built for Civil Work
01. ROADS
ITEM | UNITS | DESCRIPTION
01.01 | m3 | SITE CLEARING AND TOPSOIL STRIPPING Site clearing and topsoil stripping by mechanical methods, including topsoil excavation, bush and tree cutting, stump extraction, loading and transport to dump or acredited site. Include topsoil stockpiling near access roads for subsequent slope revegetation. Average depth 35 cm.
01.02 | m3 | CUT EXCAVATION Excavation of soil, weathered rock, or other rock, except hard rock, with the use of mechanical equipment and levelling of subgrade, and preparation and compaction of subgrade and slopes shaping. Include loading and transport to use location loading and transport to dump or acredited site.
01.03 | m3 | EMBANKMENTS Embankment construction using material from cutting excavations or borrow pit, as well as selection and internal transport. Include subgrade preparation, humidification and compaction of the material up to 95% of the modified proctor compaction test value, using vibratory compactor, in layers of thickness no more than 30 cm. Include levelling of subgrade and regrading of slopes.
01.04 | m3 | GRADED AGGREGATE SUBBASE (15 CM) Graded aggregate layer with a 15 cm thickness, with a minumum CBR of 40, including transport from crushing plant or borrowing pit, spreading out, humidification, grading and compaction at 98% of modified proctor test.
01.05 | m3 | GRADED AGGREGATE BASE (15 CM) Graded aggregate layer with a 15 cm thickness, with a minumum CBR of 60, including transport from crushing plant or borrowing pit, spreading out, humidification, grading and compaction at 98% of modified proctor test.
02. ASSEMBLY PLATAFORMS
ITEM | UNITS | DESCRIPTION
02.01 | m3 | SITE CLEARING AND TOPSOIL STRIPPING Site clearing and topsoil stripping by mechanical methods, including topsoil excavation, bush and tree cutting, stump extraction, loading and transport to dump or acredited site. Include topsoil stockpiling near access roads for subsequent slope revegetation. Average depth 35 cm.
02.02 | m3 | CUT EXCAVATION Excavation of soil, weathered rock, or other rock, except hard rock, with the use of mechanical equipment and levelling of subgrade, and preparation and compaction of subgrade and slopes shaping. Include loading and transport to use location loading and transport to dump or acredited site.
02.03 | m3 | EMBANKMENTS Embankment construction using material from cutting excavations or borrow pit, as well as selection and internal transport. Include subgrade preparation, humidification and compaction of the material up to 95% of the modified proctor compaction test value, using vibratory compactor, in layers of thickness no more than 30 cm. Include levelling of subgrade and regrading of slopes.
02.04 | m3 | GRADED AGGREGATE SUBBASE (15 - 40 CM) Graded aggregate layer with a 15 or 40 cm thickness, with a minumum CBR of 40, including transport from crushing plant or borrowing pit, spreading out, humidification, grading and compaction at 98% of modified proctor test.
02.05 | m3 | GRADED AGGREGATE BASE (15 CM) Graded aggregate layer with a 15 cm thickness, with a minumum CBR of 60, including transport from crushing plant or borrowing pit, spreading out, humidification, grading and compaction at 98% of modified proctor test.
03. ADITIONAL PLATAFORMS
ITEM | UNITS | DESCRIPTION
03.01 | m3 | SITE CLEARING AND TOPSOIL STRIPPING Site clearing and topsoil stripping by mechanical methods, including topsoil excavation, bush and tree cutting, stump extraction, loading and transport to dump or acredited site. Include topsoil stockpiling near access roads for subsequent slope revegetation. Average depth 35 cm.
03.02 | m3 | CUT EXCAVATION Excavation of soil, weathered rock, or other rock, except hard rock, with the use of mechanical equipment and levelling of subgrade, and preparation and compaction of subgrade and slopes shaping. Include loading and transport to use location loading and transport to dump or acredited site.
03.03 | m3 | EMBANKMENTS Embankment construction using material from cutting excavations or borrow pit, as well as selection and internal transport. Include subgrade preparation, humidification and compaction of the material up to 95% of the modified proctor compaction test value, using vibratory compactor, in layers of thickness no more than 30 cm. Include levelling of subgrade and regrading of slopes.
03.04 | m3 | GRADED AGGREGATE SUBBASE (15 CM) Graded aggregate layer with a 15 cm thickness, with a minumum CBR of 40, including transport from crushing plant or borrowing pit, spreading out, humidification, grading and compaction at 98% of modified proctor test.
04. FOUNDATIONS. EARTH MOVEMENTS ABOVE PEDESTAL LEVEL
ITEM | UNIDADES | DESCRIPCIÓN
04.01 | m3 | SITE CLEARING AND TOPSOIL STRIPPING Site clearing and topsoil stripping by mechanical methods, including topsoil excavation, bush and tree cutting, stump extraction, loading and transport to dump or acredited site. Include topsoil stockpiling near access roads for subsequent slope revegetation (Average depth 35 cm).
04.02 | m3 | CUT EXCAVATION Excavation of soil, weathered rock, or other rock, except hard rock, with the use of mechanical equipment and levelling of subgrade, and preparation and compaction of subgrade and slopes shaping. Include loading and transport to use location loading and transport to dump or acredited site.
05. DRAINAGE SYSTEM
ITEM | UNITS | DESCRIPTION
05.01 | m | UNLINED DRAIN TYPE 1. TRAPEZOIDAL Unlined drain without coating of 0.60 m wide and 0.60m deep trapezoidal ditches, with slope 1:1, 1.80 m width, fully finished.
05.02 | m | COATED DRAIN TYPE 1. TRAPEZOIDAL Coated drain with concrete of of 0.60 m wide and 0.60m deep trapezoidal ditches, with slope 1:1, 1.80 m width. Including shuttering, floated and joints, fully finished.
05.04 | m | COATED DRAIN TYPE 2. TRAPEZOIDAL Coated drain with concrete of 0.70 m wide and 0,70m deep trapezoidal ditches, with slope 1:1, 2.10 m width. Including shuttering, floated and joints, fully finished.
05.06 | m | COATED DRAIN TYPE 3. TRAPEZOIDAL Coated drain with concrete of .080 m wide and 0.80m deep trapezoidal ditches, with slope 1:1, 2.40 m width. Including shuttering, floated and joints, fully finished.
05.08 | m | COATED DRAIN TYPE 4. TRAPEZOIDAL Coated drain with concrete of 0.90 m wide and 0.90m deep trapezoidal ditches, with slope 1:1, 2.70 m width. Including shuttering, floated and joints, fully finished.
05.09 | Ud | CONCRETE PIPES Ø800 Supply and installation of 800mm diameter concrete pipes, including excavation of trenches in all kind of terrain, sand bed with a 10 cm thickness, fully finished.
05.10 | Ud | SIMPLE HEADWALL AND WINGS FOR CONCRETE PIPES TYPE 1. 1 X Ø800 Headwall and wings for 800mm diameter concrete pipes, fully finished and placed in work.
05.11 | Ud | SIMPLE MANHOLE FOR CONCRETE PIPES TYPE 1. 1 X Ø800 Manhole for one 800mm diameter concrete pipes, fully finished and placed in work.
05.12 | Ud | DOUBLE MANHOLE FOR CONCRETE PIPES TYPE 2. 2 X Ø800 Manhole for two 800mm diameter concrete pipes, fully finished and placed in work.
05.13 | Ud | TRIPLE MANHOLE FOR CONCRETE PIPES TYPE 3. 3 X Ø800 Manhole for three 800mm diameter concrete pipes, fully finished and placed in work.
05.14 | Ud | LOW WATER CROSSING OF CONCRETE TYPE 1 (HEIGHT 200 mm) Low warter crossing of reinforced concrete with trapezoidal section, with 4,00 m wide and 0,20 m height. Lateral slope of 25H/1V, fully finished.
05.15 | Ud | LOW WATER CROSSING OF CONCRETE TYPE 2 (HEIGHT 300 mm) Low warter crossing of reinforced concrete with trapezoidal section, with 7,00 m wide and 0,30 m height. Lateral slope of 25H/1V, fully finished.
05.16 | Ud | LOW WATER CROSSING OF CONCRETE TYPE 3 (HEIGHT 400 mm) Low warter crossing of reinforced concrete with trapezoidal section, with 9,00 m wide and 0,40 m height. Lateral slope of 25H/1V, fully finished.
05.17 | Ud | LOW WATER CROSSING OF CONCRETE TYPE 4 (HEIGHT 500 mm) Low warter crossing of reinforced concrete with trapezoidal section, with 10,00 m wide and 0,50 m height. Lateral slope of 25H/1V , fully finished.
05.18 | Ud | STRUCTURE CONCRETE BOX CULVERT TYPE 1. 3 x 2,80 m x 1,75 m Box culvert of reinforced concrete with three hollow spaces of 2,80 m x 1,75 m, fully finished.
05.19 | Ud | STRUCTURE CONCRETE BOX CULVERT TYPE 2. 1 x 2,00 m x 0,75 m Box culvert of reinforced concrete with one hollow spaces of 2,00 m x 0,75 m, fully finished.
05.20 | Ud | CUTOFF DRAIN Unlined cutoff drain without coating with approximately 0.50m wide and 0.50m deep.
06. OTHERS STRUCTURES
ITEM | UNIDADES | DESCRIPCIÓN
06.01 | Ud | GAS PIPE PROTECTION SLAB Reinforced concrete roadway slab C18/22.5/S3/IIA-LL 42.5R/0-16P, OB37, PC52 with ballast backfill and working corridor completely executed and placed on site. The approximate measurements and volumes correspond to a geometry of 12.00 m x 4.00 m according to the detailed plan and with a total thickness of 0.36 m.

## CONVENTIONAL FOUNDATIONS BoQ
SACELLE WIND FARM (ROMANIA) CONVENTIONAL WTG FOUNDATION BOQ
00. Design
ITEM | UNIT | DESCRIPTION
00.01 | un | Execution Design and As built for Conventional Foundation
WTG FOUNDATIONS
ITEM | UNITS | DESCRIPTION
01.01 | m3 | (1) FOUNDATION PIT EXCAVATION
Excavation of the foundation pit using mechanical systems in every type of terrain (except rock) and preparation and compaction of subgrade and slopes shaping. Includes transport to other areas of the site for reuse or transport to the authorized dump.
01.02 | m3 | (1) REFILL UNDER NATURAL GROUND LEVEL
Refill of the foundation, up to natural ground level, with selected material from excavation, including transport, humidification and compaction until 95% of Modified Proctor, using mechanical means in layers of 30 cm thickness. It must be ensured a dry density of 17,5kN/m3. The slope of the bakfill (2%) shall be done for drainage purposes.
01.03 | m3 | BLINDING CONCRETE C16/20
Blinding concrete with a strength class C16/20 (fck=16MPa in cylinder test tube at 28 days), mixed in concrete station, including vibration and placing with pump and vibration according to national standards. Max aggregate size: 20 mm. Slump test S2 (5-9cm settlement).
01.04 | m3 | (2) LOW PIT CONCRETE C45/55
Structural concrete for reinforced concrete, with a strength class: C45/55 (fck=45MPa in cylinder test tube at 28 days), mixed in concrete station, including pouring with pump and vibration according to national standards. Max aggregate size: 20 mm. Slump class S3 (consistency 10-15cm). Sulphate-resistant cement shall be used.
01.05 | m3 | (2) STRUCTURAL CONCRETE C30/37
Structural concrete for reinforced concrete, with a strength class: C30/37 (fck=30MPa in cylinder test tube at 28 days), mixed in concrete station, including pouring with pump and vibration according to national standards. Slump class S3 (consistency 10-15cm). Sulphate-resistant cement shall be used.
01.06 | m3 | (2) FOUNDATION PEDESTAL CONCRETE C45/55
Structural concrete for reinforced concrete, with a strength class: C45/55 (fck=45MPa in cylinder test tube at 28 days), mixed in concrete station, including pouring with pump and vibration according to national standards. Max aggregate size: 20 mm. Slump class S3 (consistency 10-15cm). Sulphate-resistant cement shall be used.
01.07 | m2 | FOUNDATION SLAB FORMWORK
Placing and removal of foundation slab formwork in concrete foundation footing.
01.08 | m2 | FOUNDATION PEDESTAL FORMWORK
Placing and removal of foundation shank formwork.
01.09 | kg | (3) CORRUGATED STEEL B500C fyk=500MPa
Corrugated steel B500C, with a minimum tensile stregth of fyk = 500 MPa. Including bending, cutting, delivered on site, all the losses due to the cut-off operations and all necessary temporary fixings and supports (binding wires, distance blocks, steel separators, etc.). Including final placement of the reinforcement according to construction drawings.
01.10 | Units | ASSEMBLY AND PLACEMENT OF ANCHOR BOLTS CAGE
Unloading, assembly and placing of anchor bolts foundation cage, provided by WTG Supplier. The price includes manpower, assembly, leveling, fixing and everything necessary for its correct execution.
01.11 | m3 | GROUTING
Preparation and pouring of grouting product to be placed under the tower flange, minimum strength class ≥ C90/105. It must be approved by WTG supplier and placed according to technical data of the product.
01.12 | m2 | SEALING OR PROTECTIVE PAINT IN PEDESTAL
Placement of the sealing exterior plastic paint, that must be UV rays and water resistant. The product is placed in the outter zone of pedestal horizontal surface and the upper 200mm of pedestal vertical surface and in the inner zone of pedestal (up to 100mm nearby the grout). Material according to WTG supplier and technical data of the product.
01.13 | m3 | (2) SOIL REPLACEMENT
Soil replacement involves complete removal of the collapsible/weak surficial soils and its replacement with soil-cement cushion. Construction of the soil-cement cushion consists of excavation to the required level, spreading cement, mixing cement into soils adding water to achieve the desired density as required, followed by compaction until the required dry density. After this, the process was repeated to build up subsequent layers.
01.14 | Units | WIND TURBINE EARTHING
Supply and laying of 50 mm² bare copper conductor (85 m for perimeter ring, 21,6 m for outer ring and 35 m for radial conductors); 9 Cadwell aluminothermic welding; 4 copper to copper mechanical connectors, 3 steel bars and soldering to the foundation rebar, 3 copper to steel bar mechanical connectors; main earthing plate; small material and connection to the main wind farm earthing, carried out according to technologist specifications, standards, drawings and as described in the manufacturer specification. It includes the protection of the bare copper cable in the bottom of the excavation with suitable backfill and tubes for the passage of grounding cables without contact with the concrete.
01.15 | Lump sum | QUALITY CONTROL
Quality control for concrete and steel according to national standards.
01.16 | Units | GEOTECHNICAL INSPECTION OF FOUNDATION BOTTOM
Geotechnical inspection on site of the foundation bottom after the excavation, carried out by a specialist geologist in order to verify if the soil properties are the ones refered in the geotechnical report and used in the foundation design.
NOTES
1 |  | Excavation slope has been estimated as 0,1H/1V and should be checked on field by specialist geologist, then excavation volume and refill volume might change.
2 |  | In the detailed design it must be checked that pedestal and slab concrete qualities are suitable.
3 |  | It must be noted that reinforcement calculation must be further calculated in a detail phase in order to achieve the exact quantity.
4 |  | The anchor bolt has been estimated and therefore the BoQ values will have to be recalculated

## PILE FOUNDATION BoQ
SACELLE WIND FARM (ROMANIA) PILE WTG FOUNDATION BOQ
00. Design
ITEM | UNIT | DESCRIPTION
00.01 | un | Execution Design and As built for Pile Foundation
WTG FOUNDATIONS
ITEM | UNITS | DESCRIPTION
01.01 | m3 | (1) FOUNDATION PIT EXCAVATION
Excavation of the foundation pit using mechanical systems in every type of terrain (except rock) and preparation and compaction of subgrade and slopes shaping. Includes transport to other areas of the site for reuse or transport to the authorized dump.
01.02 | m3 | FOUNDATION EXCAVATION FOR PILES
Excavation for piles positioning (piles 1000mm diameter), all included.
01.03 | m3 | (1) REFILL UNDER NATURAL GROUND LEVEL
Refill of the foundation, up to natural ground level, with selected material from excavation, including transport, humidification and compaction until 95% of Modified Proctor, using mechanical means in layers of 30 cm thickness. It must be ensured a dry density of 17,5kN/m3. The slope of the bakfill (2%) shall be done for drainage purposes.
01.04 | m3 | BLINDING CONCRETE C16/20
Blinding concrete with a strength class C16/20 (fck=16MPa in cylinder test tube at 28 days), mixed in concrete station, including vibration and placing with pump and vibration according to national standards. Max aggregate size: 20 mm. Slump test S2 (5-9cm settlement).
01.05 | m3 | (2) LOW PIT CONCRETE C45/55
Structural concrete for reinforced concrete, with a strength class: C45/55 (fck=45MPa in cylinder test tube at 28 days), mixed in concrete station, including pouring with pump and vibration according to national standards. Max aggregate size: 20 mm. Slump class S3 (consistency 10-15cm). Sulphate-resistant cement shall be used.
01.06 | m3 | (2) STRUCTURAL CONCRETE C30/37
Structural concrete for reinforced concrete, with a strength class: C30/37 (fck=30MPa in cylinder test tube at 28 days), mixed in concrete station, including pouring with pump and vibration according to national standards. Max aggregate size: 20 mm. Slump class S3 (consistency 10-15cm). Sulphate-resistant cement shall be used.
01.07 | m3 | (2) FOUNDATION PEDESTAL CONCRETE C45/55
Structural concrete for reinforced concrete, with a strength class: C45/55 (fck=45MPa in cylinder test tube at 28 days), mixed in concrete station, including pouring with pump and vibration according to national standards. Max aggregate size: 20 mm. Slump class S3 (consistency 10-15cm). Sulphate-resistant cement shall be used.
01.08 | m3 | (3) PILES STRUCTURAL CONCRETE C30/37
Structural concrete for reinforced concrete, with a strength class: C30/37 (fck=30MPa in cylinder test tube at 28 days), mixed in concrete station, including pouring with pump and vibration according to national standards.
01.09 | m2 | FOUNDATION SLAB FORMWORK
Placing and removal of foundation slab formwork in concrete foundation footing.
01.10 | m2 | FOUNDATION PEDESTAL FORMWORK
Placing and removal of foundation shank formwork.
01.11 | kg | (3) CORRUGATED STEEL B500C fyk=500MPa
Corrugated steel B500C, with a minimum tensile stregth of fyk = 500 MPa. Including bending, cutting, delivered on site, all the losses due to the cut-off operations and all necessary temporary fixings and supports (binding wires, distance blocks, steel separators, etc.). Including final placement of the reinforcement according to construction drawings.
01.12 | kg | (3) CORRUGATED STEEL B500C fyk=500MPa FOR PILES
Corrugated steel B500C, with a minimum tensile stregth of fyk = 500 MPa. Including bending, cutting, delivered on site, all the losses due to the cut-off operations and all necessary temporary fixings and supports (binding wires, distance blocks, steel separators, etc.). Including final placement of the reinforcement according to construction drawings.
01.13 | Units | ASSEMBLY AND PLACEMENT OF ANCHOR BOLTS CAGE
Unloading, assembly and placing of anchor bolts foundation cage, provided by WTG Supplier. The price includes manpower, assembly, leveling, fixing and everything necessary for its correct execution.
01.14 | m3 | GROUTING
Preparation and pouring of grouting product to be placed under the tower flange, minimum strength class ≥ C90/105. It must be approved by WTG supplier and placed according to technical data of the product.
01.15 | m2 | SEALING OR PROTECTIVE PAINT IN PEDESTAL
Placement of the sealing exterior plastic paint, that must be UV rays and water resistant. The product is placed in the outter zone of pedestal horizontal surface and the upper 200mm of pedestal vertical surface and in the inner zone of pedestal (up to 100mm nearby the grout). Material according to WTG supplier and technical data of the product.
01.16 | Units | WIND TURBINE EARTHING
Supply and laying of 50 mm² bare copper conductor (80,4 m for perimeter ring, 21,4 m for outer ring and 33 m for radial conductors); 9 Cadwell aluminothermic welding; 4 copper to copper mechanical connectors, 3 steel bars and soldering to the foundation rebar, 3 copper to steel bar mechanical connectors; main earthing plate; small material and connection to the wind farm main earthing, carried out according to technologist specifications, standards, drawings and as described in the manufacturer specification. It includes the protection of the bare copper cable in the bottom of the excavation with suitable backfill and tubes for the passage of grounding cables without contact with the concrete.
01.17 | Lump sum | QUALITY CONTROL
Quality control for concrete and steel according to national standards.
01.18 | Units | GEOTECHNICAL INSPECTION OF FOUNDATION BOTTOM
Geotechnical inspection on site of the foundation bottom after the excavation, carried out by a specialist geologist in order to verify if the soil properties are the ones refered in the geotechnical report and used in the foundation design.
NOTES
1 |  | Excavation slope has been estimated as 0,1H/1V and should be checked on field by specialist geologist, then excavation volume and refill volume might change.
2 |  | In the detailed design it must be checked that pedestal and slab concrete qualities are suitable.
3 |  | It must be noted that reinforcement calculation must be further calculated in a detail phase in order to achieve the exact quantity.
4 |  | The anchor bolt has been estimated and therefore the BoQ values will have to be recalculated