| BIDDER |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| PROVIDER |  |  |  |  |  |  |
| PRODUCT CODE |  |  | N/A |  |  |  |
| TYPE |  |  | A2XS2Y/NA2XS2Y |  |  |  |
| The construction of the cables will comply with the provisions SR EN 60228:2005+AC:2014, IEC 60502-2:2014, SR EN 60811-100:2012+ other sections |  |  |  |  |  |  |
| Specifications |  |  | UN | Values |  | Note |
|  |  |  |  | Necessary | Guarantee |  |
| 1. Climatic and environmental conditions |  |  |  |  |  |  |
| 1 | Installation place |  | - | exterior |  |  |
| 2 | Altitude |  | m | Max.1000 |  |  |
| 3 | Ambient air temperature | maxim | ºC | +40 |  |  |
| 4 |  | medium (24h) | ºC | +15 |  |  |
| 5 |  | Minimum | ºC | -30 |  |  |
| 6 | Maximum relative humidity at 20C |  | % | 100 |  |  |
| 2. Conditions imposed by the energy system |  |  |  |  |  |  |
| 1 | Nominal frequency |  | Hz | 50 |  |  |
| 2 | Nominal system voltage |  | kV | 35 |  |  |
| 3 | Maximum system operating voltage |  | kV | 40,5/42 |  |  |
| 4 | 35 kV mains neutral connection |  |  | Neutral treated by Rn |  |  |
| 5 | Maximum duration of earth defects |  | sec | 3 |  |  |
| 3. Electrical characteristics |  |  |  |  |  |  |
| 1 | Rated voltage Uo/Un |  | kV | 20,8/36 |  |  |
| 2 | Izolation level: - Lightning pulse - Switching pulse - Runaway line length |  | kVmax cold cm/kV | 125 90 2,0 |  |  |
| 3 | The maximum current-carrying capacity in: - earth in trefoil - in the air |  | A | Yes Yes |  |  |
| 3 | Material conductor activ |  |  | Multi-strand conductors made of Al, twisted and Compacted Class 2 |  |  |
| 5 | The maximum permissible temperature of the conductor at the normal conduct |  | ºC | 90 |  |  |
| 6 | Maximum temperature per conductor at overload (8 hours consecutive, but not more than 125 hours/year) |  | ºC | 130 |  |  |
| 7 | Maximum permissible temperature in short-circuit conditions |  | ºC | 250 |  |  |
| 8 | Level of partial discharges |  | pC | max. 5 |  |  |
| 9 | Minimum installation temperature |  | °C | -20 |  |  |
| 10 | Minimum operating temperature |  | °C | -30 |  |  |
| 11 | Characteristics of the insulation material: Type according to Material |  | - - | SR EN 60502 XPLE |  |  |
| 12 | Nominal insulation thickness |  | min mm | 5,5 |  |  |
| 13 | Semiconductor Tape |  |  | Yes |  |  |
| 14 | Copper wire screen wrapped in copper strip |  |  | Yes |  |  |
| 15 | Separator layer |  |  | Yes |  |  |
| 16 | Barrier against water ingress - Longitudinal - Cross |  |  | yesyes |  |  |
| 17 | Mantel material |  |  | PE |  |  |
| 18 | Outer semi-conductiong layer - extruded interior - extruded exterior |  |  | Yes yes |  |  |
| 19 | Mechanical characteristics : - Minimum breaking load - Conduting material - Conductor section - Screen material - Screen section |  | kg - mmp - - mmp | 2500 Al 70 185 240 630 Cooper 16 / 25 / 35 |  |  |
| 20 | Radius of curvature when laying |  |  | 15xD |  |  |
| 4. Maintenance and reliability conditions |  |  |  |  |  |  |
| 1 | Maintenance conditions: - lifespan; - failure rate |  | Year %/year | ≥ 30 ≤ 0,005 |  |  |
| 2 | Parameter(s) indicated by the manufacturer for checking the in-service condition |  |  | Yes |  |  |
| 3 | The duration at which the manufacturer recommends checking the condition in service |  |  | Yes |  |  |
| 5. Delivery, packaging and storage conditions |  |  |  |  |  |  |
| 1 | Transport and storage conditions |  | - | Yes |  |  |
| 2 | Individual Seekers |  | - | CEI conf. Standard CS |  |  |
| 3 | Type tests |  | - | CEI conf. Standard |  |  |
| 4 | Name of the test laboratory |  |  | Yes |  |  |
| 6. Technical documentation that will be delivered with the product |  |  |  |  |  |  |
| 1 | List of maintenance tests, their periodicity; Recommended specialized tools and devices. |  | - | Yes |  |  |
| 2 | Installation, operation, maintenance procedures; |  | - | Yes |  |  |
| 3 | Certificate of conformity (quality certificate) |  | - | Yes |  |  |
| 4 | Warranty certificate and the date from which time begins to run |  | - | Yes |  |  |
| 7. Quality Assurance Conditions |  |  |  |  |  |  |
| 1 | Conditions for ensuring quality, environmental protection, health and safety at work in accordance with: ISO 9001, ISO 14001, OHSAS 18001 and the quality, environment and occupational health standards associated with them. |  | - | Conf. ISO 9000-9004 |  |  |
| 2 | List of standard quality requirements during design, production, testing |  | - | Of |  |  |
| 3 | List of routine tests |  | - | Of |  |  |
| 8. Warranty conditions |  |  |  |  |  |  |
| 1 | Warranty conditions from delivery |  | - | Min. 24 months |  |  |
| 2 | Warranty conditions from commissioning |  | - | Min. 24 months |  |  |
| 9. Other conditions |  |  |  |  |  |  |
| 1 | Delivery conditions |  | - | IEC-694 |  |  |
| 2 | Packaging conditions |  | - | IEC-694 |  |  |
| 3 | Conditions of Carriage |  | - | IEC-694 |  |  |
| 4 | List of recommended spare parts and special tools |  | - | Yes |  |  |
| 5 | List of type, individual and site tests |  | - | Yes |  |  |
| 6 | Test Sample Certificates |  | - | Yes |  |  |